## 1. Advantages of ETSW
Potential Advantages of ETSW Procedure:
1. Reduction in backwash water usage
2. Reduction or elimination of the need for filter-to-waste (or rewash)
3. Improves visual observation of the filter media and structures
4. Reduction or elimination of the degraded filtered water quality during the filter ripening period
5. Improves reducttion of pathogens from filters prior to restart
6. Decreases hydraulic loading of recycle streams
7. Could lengthen the life of backwash pumps and underdrain systems
8. A tool for complying with Partnership for Safe Water program guidelines on turbidity
9. The production of safer and cleaner drinking water for consumers
10. Actually makes the filter "look" clean before returning it to service
Potential Disadvantages of ETSW Procedure:
1. Might require a few extra minutes to complete the backwash procedure
2. Could require the addition of a new step to the original backwash procedure
Software is provided as a courtesy of:
Water Treatment Research, Inc.
LEGAL DISCLAIMER:
Software is provided for informational purposes only. The resale of this software is prohibited.
Users accept full responsibility for all actions influenced by the use or misuse of this software.
Always use good engineering judgement and common sense when modifying water treatment operations.
INDEMNIFICATION:
You hereby agree to indemnify and hold harmless WTR, Inc. from and against any and all claims, charges, demands, damages, liabilities, losses, expenses, and liabilities of whatever nature and howsoever arising (including but not limited to any legal or
other professional fees and the costs of defending or prosecuting any claim and any loss of profit, goodwill, and any other direct or consequential loss) incurred or suffered by WTR, Inc. directly or indirectly by reason of any act or omission which you commit
in breach of these terms and conditions and the obligations and warranties contained in them.

## 2. Software Instructions
SOFTWARE INSTRUCTIONS:
1. Read the sheet titled "Application Notes" carefully.
2. Collect the necessary data to fill in the greeen values on the "MAIN (START)+Summary" tab
3. Input the necessary data on the "MAIN (START)+Summary" tab (yellow fields)
4. Some initial recommendations are provided on the "MAIN (START)+Summary" tab (blue fields)
5. With the ETSW procedure, it is generally best to start at the lowest recommended ETSW rate and begin working
your way upward to decrease the total duration of the ETSW procedure.
6. The lowest ETSW rate is the below the minimum fluidization velocity of the easiest to fluidize type of media at the
coldest water temperature encountered by your utility. It is possible to change ETSW rates seasonally as the
viscosity of the water changes, and the same type of change is recommended for the fluidization stage of backwashing.
7. Individual parts of this spreadsheet are designated for determining the minimum fluidization velocity of the smallest and
largest sizes of media grains contained within a filter. Two sheets are included for calculating parameters for 2 types
of filter media. The smallest grains of both medias NOT being fluidized is important to the ETSW process, and the
largest grains of both types of media BEING fluidized is important to fluidization stage of backwashing
8. The "ETSW Time" portion of the spreadsheet shows all of the data necessary used to estimate the ETSW time. Some
of these values are assumed as typical to simplify the use of this spreadsheet, but the values can be changed as
to better predict time. The factor of safety is also optional and can be used or changed at your discretion
9. Some typical values, constants, conversion sheets, and a sample backwash protocol are also included for your
convenience.
10.Any problems, questions, or suggestions can be directed to Dr. James Amburgey (jeamburg@uncc.edu)
Helpful Hint: No values are hidden or protected, so be careful not to erroneosly change or delete any critical values

## 3. Application Notes
Application Notes:
1. The "Data Required-Summary Page" is intended to provide some quick estimates of ETSW rates and times based on
both the data provided by the user and some typical values (that are already stored in the spreadsheet)
2. ETSW rate will change with water temperature just as fluidization rate does, and specific worksheets are devoted
to the the temperature dependency of ETSW and Fluidization rates for two types of filter media (one of which will be the
limiting case) ETSW is often limited by the lower of the two values and fluidization by the higher value of the two
3. ETSW rates also depend on the strength of the floc, so what works well at one facility may not work well at a similar
facility (even if both facilities have the same media design and water temperature)
4. ETSW times will change based on the ETSW rate, the amount of dispersion that occurs, and the uneven distribution
of backwash water throughout the entire filter bed
5. The optimality of the coagulation process also impacts the ETSW procedure and the resulting filter ripening turbidity
spikes since the ETSW procedure does not remove ALL backwash remnant particles. The proportion of remaining
backwash remnant particles that return through the filter into the finished water will depend upon the charge (zeta potential)
of the backwash remnant particles
6. Implementation of the ETSW procedure will require the use of some common sense and likely some trial and error
Good Luck! | *Many helpful comments are provided in red text throughout the spreadsheet
*User Input parameters are typically in green text throughout with yellow backgrounds
*Most calculated values appear in blue text (metric and english units are sometimes both provided)

## 4. MAIN (START)+Summary
Parameter | Description | Value | Units
Effective Size (ES) | sand | 0.52 | mm |  | <==User Input Values
Uniformity Coefficient (UC) | sand | 1.53 | d60/d10
Media Density | sand | 2.65 | g/cm^3 |  | Based on the information provided to the left:
Media Depth (D) | sand | 1 | feet |  | Your recommended initial fludization rate would be: |  |  |  | 7888.5878 | gpm | for at least | 4.9692 | minutes
[5 empty] | Step #1, start with an ETSW (subfluidization) rate of: |  |  |  | 1119.0366 | gpm | for at least | 12.8401 | minutes
Effective Size (ES) | anthracite | 1.01 | mm |  | Step #2, with ripening peaks < 0.10 NTU, try an ETSW of: |  |  |  | 1865.0125 | gpm | for at least | 7.7042 | minutes
Uniformity Coefficient (UC) | anthracite | 1.49 | d60/d10 |  | Step #3, with ripening peaks < 0.10 NTU, try ETSW up to: |  |  |  | 4051.7585 | gpm | for at least | 3.5462 | minutes
Media Density | anthracite | 1.55 | g/cm^3 |  | *Use a lower ETSW rate whenever filter ripening turbidity exceeds goal (or ~0.10 NTU)
Media Depth (D) | anthracite | 1.5 | feet |  | **Find a more optimal coagulant dose/pH combo when turbidity exceeds 0.10 NTU after 1 filter volume
Freeboard (top of media to overflow) | filter at rest | 3 | feet | Width (ft) | Length (ft) | Area (ft^2)
Surface Area of Filter (or one side) | basis for flows | 392 | sq. ft. | 14 | 28 | 392
Water Temperature | for your use!* | 12 | °C | -ETSW and Fluidization rate values should both change signficantly with water temperature as indicated below
SUMMARY INFORMATION: (please scroll down) |  |  |  |  | Approximate
| Sand | Anthracite | Average | Units | ETSW Time | Units
Recommended Initial ETSW rate | 2.5463 | 3.1631 | 2.8547 | gpm/sf | 12.8401 | minutes | <==Initial Recommended ETSW Values (gpm/sf)
Reasonable Initial ETSW rate (25° C) | 4.2843 | 5.2311 | 4.7577 | gpm/sf | 7.7042 | minutes |  | Your final value will depend on your filtered water turbidity during the ripening period relative to your goal.
Max Recommended ETSW rate | 9.938 | 10.7342 | 10.3361 | gpm/sf | 3.5462 | minutes |  | This value could increase or decrease as water temperature and coagulation conditions vary.
Absolute Maximum ETSW rate (25° C) | 15.3603 | 15.5996 | 15.48 | gpm/sf | 2.3679 | minutes
Approximate
| Sand | Anthracite | Average | Units | ETSW Time | Units
Recommended Initial ETSW rate | 998.1412 | 1239.932 | 1119.0366 | gpm | 12.8401 | minutes | <==Initial Recommended ETSW Values (gpm)
Reasonable Initial ETSW rate (25° C) | 1679.4279 | 2050.5971 | 1865.0125 | gpm | 7.7042 | minutes |  | Your final value will depend on your filtered water turbidity during the ripening period relative to your goal.
Max Recommended ETSW rate | 3895.6919 | 4207.825 | 4051.7585 | gpm | 3.5462 | minutes |  | This value could increase or decrease as water temperature and coagulation conditions vary.
Absolute Maximum ETSW rate (25° C) | 6021.2461 | 6115.0428 | 6068.1445 | gpm | 2.3679 | minutes
Minimum Rec. Fluidization
| Rate | Units | Temp. | Units | Time | Units
Recommended Fluidization Rate | 13.437 | gpm/sf | 5 | °C | 7.4422 | minutes
Recommended Fluidization Rate | 15.1769 | gpm/sf | 10 | °C | 6.589 | minutes
Recommended Fluidization Rate | 16.8761 | gpm/sf | 15 | °C | 5.9256 | minutes
Recommended Fluidization Rate | 18.536 | gpm/sf | 20 | °C | 5.3949 | minutes
Recommended Fluidization Rate | 20.1239 | gpm/sf | 25 | °C | 4.9692 | minutes | <==Initial Recommended Hi-Rate (Fluidization) Backwashing Values (gpm/sf)
Recommended Fluidization Rate | 21.6141 | gpm/sf | 30 | °C | 4.6266 | minutes |  | Your final values should change with water temperature, but you could default to the maximum water temperature and let the bed expansion vary.
These values could be increased or decreased based on a solids retention analaysis of the media.
Minimum Rec. Fluidization
| Rate | Units | Temp. | Units | Time | Units
Recommended Fluidization Rate | 5267.286 | gpm | 5 | °C | 7.4422 | minutes
Recommended Fluidization Rate | 5949.3384 | gpm | 10 | °C | 6.589 | minutes
Recommended Fluidization Rate | 6615.4184 | gpm | 15 | °C | 5.9256 | minutes
Recommended Fluidization Rate | 7266.107 | gpm | 20 | °C | 5.3949 | minutes
Recommended Fluidization Rate | 7888.5878 | gpm | 25 | °C | 4.9692 | minutes | <==Initial Recommended Hi-Rate (Fluidization) Backwashing Values (gpm)
Recommended Fluidization Rate | 8472.7427 | gpm | 30 | °C | 4.6266 | minutes |  | Your final values should change with water temperature, but you could default to the maximum water temperature and let the bed expansion vary.
These values could be increased or decreased based on a solids retention analaysis of the media.

## 5. Sample ETSW BWash Proc.
Start Time | Action | Flow Rate | Units | Duration | Units
Close Filter Influent Valve
Drop water level in filter to 6" above the media
Close Filter Effluent Valve
Open Washwater Drain Valve
Open Air Wash Valve
0:00 | Start Air Wash Blower | 784 | scfm
0:00 | Open Wash Water Valve
0:00 | Start Wash Water Pump
0:00 | Set flow to: | 1664.0322 | gpm |  |  | Water level rise: |  | Available: |  | Remaining:
0:01 | Combined Air & Water Wash | 1664.0322 | gpm | 3 | minutes | 1.7025 | ft | 3 | ft | 1.2975 | ft
3:00 | Air Off/ Close Air Valve
| Allow air bubbles to escape from the filter bed |  |  | 1 | minutes
4:00 | Set flow rate to: | 4051.7585 | gpm
4:30 | Flow rate reaches set point |  |  | 0.5 | minutes
4:31 | Low rate wash | 4051.7585 | gpm | 0.5 | minutes
5:00 | Set flow rate to: | 7888.5878 | gpm
5:30 | Flow rate reaches set point |  |  | 0.5 | minutes
6:00 | Media transitions to fluidized bed |  |  | 0.5 | minutes
| High Rate Fluidized Bed Backwash | 7888.5878 | gpm | 4.9692 | minutes
11:00 | Set flow rate to: | 1119.0366 | gpm
11:30 | Flow rate reaches set point |  |  | 0.5 | minutes
12:00 | Media transitions to fixed bed |  |  | 0.5 | minutes
| ETSW (Subfluidized Wash for 1 filter volume) | 1119.0366 | gpm | 12.8401 | minutes
25:00 | Set washwater rate to 0 gpm
Close washwater valve and turn off pump
Proceed to other bay of Filter or Refill and Restart
NOTES ON ETSW IMPLEMENTATION:
If air scour or surface wash is used as the primary method of cleaning the filter and the
fluidization step is mainly for removing the detached solids from the filter box, THEN shortening
the duration of the fluidization step (from the non-ETSW procedure) may be most appropriate.
HOWEVER, if fluidization is the primary means of cleaning the filter, then shortening the duration
of the fluidization step may NOT be appropriate as the cleaning efficiency may suffer. In this case,
simply add the ETSW step to the end of the original backwash procedure.

## 6. ETSW Time
Detention Time at: X (gpm/sf)
Filter Component | Depth (ft) | Porosity | Void Space (ft^3/ft^2) | Void Vol (gal/sf) | 2.8547 | 4.7577 | 5 | 6 | 10.3361 | 15.48
Underdrain | 1 | 0.95 | 0.95 | 7.1079 | 2.4899 | 1.494 | 1.4216 | 1.1847 | 0.68768 | 0.45917
Gravel | 1 | 0.5 | 0.5 | 3.741 | 1.3105 | 0.78631 | 0.7482 | 0.6235 | 0.36194 | 0.24167
Sand | 1 | 0.42 | 0.42 | 3.1424 | 1.1008 | 0.6605 | 0.62849 | 0.52374 | 0.30403 | 0.203
Anthracite | 1.5 | 0.56 | 0.84 | 6.2849 | 2.2016 | 1.321 | 1.257 | 1.0475 | 0.60805 | 0.406
Media to overflow | 3 | 1 | 3 | 22.446 | 7.8629 | 4.7178 | 4.4892 | 3.741 | 2.1716 | 1.45
Totals: | 7.5 |  | 5.71 | 42.7223 | 14.9657 | 8.9796 | 8.5445 | 7.1204 | 4.1333 | 2.7598
ETSW-minimum (minutes): |  |  |  |  | 11.1653 | 6.6993 | 6.3747 | 5.3122 | 3.0837 | 2.059
ETSW (minutes) with x1.3 factor to account for dispersion: |  |  |  |  | 14.5149 | 8.7092 | 8.2871 | 6.9059 | 4.0088 | 2.6767

## 7. Fluidization Time
Source: Cleasby and Logsdon in Water Quality and Treatment, 5th Ed.
Typical values: Use 100 to 200 gallons per square foot per backwash
Water Usage (gallons/sq.ft.): | 100 | 125 | 150 | 175 | 200
Backwash Rate (gpm/sf) | Time for Rate to yield corresponding water use (minutes)
10 | 10 | 12.5 | 15 | 17.5 | 20
11 | 9.0909 | 11.3636 | 13.6364 | 15.9091 | 18.1818
12 | 8.3333 | 10.4167 | 12.5 | 14.5833 | 16.6667
13 | 7.6923 | 9.6154 | 11.5385 | 13.4615 | 15.3846
13.437 | 7.4422 | 9.3027 | 11.1632 | 13.0238 | 14.8843
15.1769 | 6.589 | 8.2362 | 9.8835 | 11.5307 | 13.1779
16.8761 | 5.9256 | 7.4069 | 8.8883 | 10.3697 | 11.8511
18.536 | 5.3949 | 6.7436 | 8.0924 | 9.4411 | 10.7898
20.1239 | 4.9692 | 6.2115 | 7.4538 | 8.6961 | 9.9384
21.6141 | 4.6266 | 5.7833 | 6.9399 | 8.0966 | 9.2532
23 | 4.3478 | 5.4348 | 6.5217 | 7.6087 | 8.6957
25 | 4 | 5 | 6 | 7 | 8
*The 100 gallons per sq. ft. per wash column is probably a good starting point for
a fluidization time when the ETSW procedure is used, since an additional volume
of water will be used for the ETSW step, low-rate washes, and transitionary flow
between setpoints…
** Depending on media size (thus fluidization velocity), the amount of freeboard
in a particular filter design, the water temperature, and the presence of air scour
backwashing or surface washing; adequate and optimal fluidization times can
vary widely between facilities

## 8. ETSW-Sand
Input Parameters | Value | Units | Calculated Parameter | Value | Units
Effective Size (ES) (d-10) | 0.52 | mm
Uniformity Coefficient (UC) | 1.53
|  |  | d-10 size | 0.52 | mm
Media density (rho-s) | 2.65 | g/cm^3
CONSTANTS:
Dynamic Viscosity
mu (0) | 0.01781 | g/(cm)(s) | Galileo Number (0) | 717.4653 | none
mu (5) | 0.01519 | g/(cm)(s) | Galileo Number (5) | 986.3872 | none
mu (10) | 0.01307 | g/(cm)(s) | Galileo Number (10) | 1332.1725 | none
mu (15) | 0.01139 | g/(cm)(s) | Galileo Number (15) | 1753.7243 | none
mu (20) | 0.01002 | g/(cm)(s) | Galileo Number (20) | 2265.263 | none
mu (25) | 0.0089 | g/(cm)(s) | Galileo Number (25) | 2869.9018 | none
mu (30) | 0.00798 | g/(cm)(s) | Galileo Number (30) | 3567.9276 | none
Density
rho (0) | 0.9998 | g/cm^3 | Vmf (0) | 0.14783 | cm/s
rho (5) | 1 | g/cm^3 | Vmf (5) | 0.1729 | cm/s
rho (10) | 0.9997 | g/cm^3 | Vmf (10) | 0.20038 | cm/s
rho (15) | 0.9991 | g/cm^3 | Vmf (15) | 0.22919 | cm/s
rho (20) | 0.9982 | g/cm^3 | Vmf (20) | 0.25953 | cm/s
rho (25) | 0.997 | g/cm^3 | Vmf (25) | 0.29092 | cm/s
rho (30) | 0.9957 | g/cm^3 | Vmf (30) | 0.32285 | cm/s
acceleration due to gravity | 981 | cm/s^2 | CONVERTED UNITS:
|  |  | Vmf (0°C) | 5.3221 | m/hr
|  |  | Vmf (5°C) | 6.2245 | m/hr
|  |  | Vmf (10°C) | 7.2137 | m/hr
|  |  | Vmf (15°C) | 8.2507 | m/hr
|  |  | Vmf (20°C) | 9.3431 | m/hr
|  |  | Vmf (25°C) | 10.4731 | m/hr
|  |  | Vmf (30°C) | 11.6225 | m/hr
|  |  | Vmf (0°C) | 2.1771 | gpm/sf
Recommended Initial ETSW Rate ===========> |  |  | Vmf (5°C) | 2.5463 | gpm/sf
*you may choose to average the sand and |  |  | Vmf (10°C) | 2.9509 | gpm/sf
anthracite values for dual media filters, or you |  |  | Vmf (15°C) | 3.3751 | gpm/sf
can choose the lowest value (to be on the safe |  |  | Vmf (20°C) | 3.822 | gpm/sf
side) and gradually work up from there to shorten |  |  | Vmf (25°C) | 4.2843 | gpm/sf
the backwash duration. |  |  | Vmf (30°C) | 4.7544 | gpm/sf

## 9. ETSW-Anthr
Input Parameters | Value | Units | Calculated Parameter | Value | Units
Effective Size (ES) (d-10) | 1.01 | mm
Uniformity Coefficient (UC) | 1.49
|  |  | d-10 size | 1.01 | mm
Media density (rho-s) | 1.55 | g/cm^3
CONSTANTS:
Dynamic Viscosity
mu (0) | 0.01781 | g/(cm)(s) | Galileo Number (0) | 1752.8268 | none
mu (5) | 0.01519 | g/(cm)(s) | Galileo Number (5) | 2409.2411 | none
mu (10) | 0.01307 | g/(cm)(s) | Galileo Number (10) | 3255.0012 | none
mu (15) | 0.01139 | g/(cm)(s) | Galileo Number (15) | 4288.1248 | none
mu (20) | 0.01002 | g/(cm)(s) | Galileo Number (20) | 5544.9412 | none
mu (25) | 0.0089 | g/(cm)(s) | Galileo Number (25) | 7035.1507 | none
mu (30) | 0.00798 | g/(cm)(s) | Galileo Number (30) | 8759.9319 | none
Density
rho (0) | 0.9998 | g/cm^3 | Vmf (0) | 0.18428 | cm/s
rho (5) | 1 | g/cm^3 | Vmf (5) | 0.21479 | cm/s
rho (10) | 0.9997 | g/cm^3 | Vmf (10) | 0.24801 | cm/s
rho (15) | 0.9991 | g/cm^3 | Vmf (15) | 0.28251 | cm/s
rho (20) | 0.9982 | g/cm^3 | Vmf (20) | 0.31846 | cm/s
rho (25) | 0.997 | g/cm^3 | Vmf (25) | 0.35522 | cm/s
rho (30) | 0.9957 | g/cm^3 | Vmf (30) | 0.39204 | cm/s
acceleration due to gravity | 981 | cm/s^2 | CONVERTED UNITS:
|  |  | Vmf (0°C) | 6.6342 | m/hr
|  |  | Vmf (5°C) | 7.7324 | m/hr
|  |  | Vmf (10°C) | 8.9282 | m/hr
|  |  | Vmf (15°C) | 10.1702 | m/hr
|  |  | Vmf (20°C) | 11.4646 | m/hr
|  |  | Vmf (25°C) | 12.7878 | m/hr
|  |  | Vmf (30°C) | 14.1135 | m/hr
|  |  | Vmf (0°C) | 2.7139 | gpm/sf
Recommended Initial ETSW Rate ===========> |  |  | Vmf (5°C) | 3.1631 | gpm/sf
*you may choose to average the sand and |  |  | Vmf (10°C) | 3.6523 | gpm/sf
anthracite values for dual media filters, or you |  |  | Vmf (15°C) | 4.1603 | gpm/sf
can choose the lowest value (to be on the safe |  |  | Vmf (20°C) | 4.6898 | gpm/sf
side) and gradually work up from there to shorten |  |  | Vmf (25°C) | 5.2311 | gpm/sf
the backwash duration. |  |  | Vmf (30°C) | 5.7734 | gpm/sf

## 10. Vmf-Sand
Input Parameters | Value | Units | Calculated Parameter | Value | Units
Effective Size (ES) (d-10) | 0.52 | mm
Uniformity Coefficient (UC) | 1.53
|  |  | d-90 size | 1.0579 | mm
Media density (rho-s) | 2.65 | g/cm^3
CONSTANTS:
Dynamic Viscosity
mu (0) | 0.01781 | g/(cm)(s) | Galileo Number (0) | 6040.9464 | none
mu (5) | 0.01519 | g/(cm)(s) | Galileo Number (5) | 8305.2269 | none
mu (10) | 0.01307 | g/(cm)(s) | Galileo Number (10) | 11216.685 | none
mu (15) | 0.01139 | g/(cm)(s) | Galileo Number (15) | 14766.0857 | none
mu (20) | 0.01002 | g/(cm)(s) | Galileo Number (20) | 19073.1617 | none
mu (25) | 0.0089 | g/(cm)(s) | Galileo Number (25) | 24164.1268 | none
mu (30) | 0.00798 | g/(cm)(s) | Galileo Number (30) | 30041.3954 | none
Density
rho (0) | 0.9998 | g/cm^3 | Vmf (0) | 0.58556 | cm/s
rho (5) | 1 | g/cm^3 | Vmf (5) | 0.67483 | cm/s
rho (10) | 0.9997 | g/cm^3 | Vmf (10) | 0.76828 | cm/s
rho (15) | 0.9991 | g/cm^3 | Vmf (15) | 0.86116 | cm/s
rho (20) | 0.9982 | g/cm^3 | Vmf (20) | 0.95342 | cm/s
rho (25) | 0.997 | g/cm^3 | Vmf (25) | 1.043 | cm/s
rho (30) | 0.9957 | g/cm^3 | Vmf (30) | 1.1284 | cm/s
acceleration due to gravity | 981 | cm/s^2 | CONVERTED UNITS:
|  |  | Vmf (0°C) | 21.0801 | m/hr
|  |  | Vmf (5°C) | 24.2941 | m/hr
|  |  | Vmf (10°C) | 27.6579 | m/hr
|  |  | Vmf (15°C) | 31.0016 | m/hr
|  |  | Vmf (20°C) | 34.3232 | m/hr
|  |  | Vmf (25°C) | 37.5493 | m/hr
|  |  | Vmf (30°C) | 40.621 | m/hr
|  |  | Vmf (0°C) | 8.6233 | gpm/sf
Recommended Maximum ETSW Rate ========> |  |  | Vmf (5°C) | 9.938 | gpm/sf
*you may choose to exceed this value in favor of |  |  | Vmf (10°C) | 11.3141 | gpm/sf
the Vmf for 25 degrees C during the summer |  |  | Vmf (15°C) | 12.6819 | gpm/sf
months and then revert back to this value during |  |  | Vmf (20°C) | 14.0406 | gpm/sf
the winter months. |  |  | Vmf (25°C) | 15.3603 | gpm/sf
|  |  | Vmf (30°C) | 16.6169 | gpm/sf
|  | Temp. (C) | Recommended Wash Rates (1.3*Vmf)
|  | 0 | 27.4041 | m/hr | Ratio to 20 C
|  | 5 | 31.5823 | m/hr | 0.7078
|  | 10 | 35.9553 | m/hr | 0.80581
|  | 15 | 40.3021 | m/hr | 0.90323
|  | 20 | 44.6202 | m/hr | 1
|  | 25 | 48.8141 | m/hr | 1.094
|  | 30 | 52.8073 | m/hr | 1.1835
|  | 0 | 11.2102 | gpm/sf | 0.61416
*lower backwash rates can be used |  | 5 | 12.9194 | gpm/sf | 0.7078
when water is colder to conserve |  | 10 | 14.7083 | gpm/sf | 0.80581
backwash water, with little concern |  | 15 | 16.4864 | gpm/sf | 0.90323
over decreasing cleaning efficiency |  | 20 | 18.2528 | gpm/sf | 1
Recommended Backwash Rate ===> |  | 25 | 19.9684 | gpm/sf | 1.094
|  | 30 | 21.6019 | gpm/sf | 1.1835
*again, you can average values for sand and anthracite, or choose the higher value to be on the safe side

## 11. Vmf-Anthracite
Input Parameters | Value | Units | Calculated Parameter | Value | Units
Effective Size (ES) (d-10) | 1.01 | mm
Uniformity Coefficient (UC) | 1.49
|  |  | d-90 size | 1.9658 | mm
Media density (rho-s) | 1.55 | g/cm^3
CONSTANTS:
Dynamic Viscosity
mu (0) | 0.01781 | g/(cm)(s) | Galileo Number (0) | 12924.1566 | none
mu (5) | 0.01519 | g/(cm)(s) | Galileo Number (5) | 17764.1109 | none
mu (10) | 0.01307 | g/(cm)(s) | Galileo Number (10) | 24000.1725 | none
mu (15) | 0.01139 | g/(cm)(s) | Galileo Number (15) | 31617.7249 | none
mu (20) | 0.01002 | g/(cm)(s) | Galileo Number (20) | 40884.6376 | none
mu (25) | 0.0089 | g/(cm)(s) | Galileo Number (25) | 51872.432 | none
mu (30) | 0.00798 | g/(cm)(s) | Galileo Number (30) | 64589.7995 | none
Density
rho (0) | 0.9998 | g/cm^3 | Vmf (0) | 0.64155 | cm/s
rho (5) | 1 | g/cm^3 | Vmf (5) | 0.7289 | cm/s
rho (10) | 0.9997 | g/cm^3 | Vmf (10) | 0.81723 | cm/s
rho (15) | 0.9991 | g/cm^3 | Vmf (15) | 0.90186 | cm/s
rho (20) | 0.9982 | g/cm^3 | Vmf (20) | 0.983 | cm/s
rho (25) | 0.997 | g/cm^3 | Vmf (25) | 1.0593 | cm/s
rho (30) | 0.9957 | g/cm^3 | Vmf (30) | 1.1296 | cm/s
acceleration due to gravity | 981 | cm/s^2 | CONVERTED UNITS:
|  |  | Vmf (0°C) | 23.0959 | m/hr
|  |  | Vmf (5°C) | 26.2406 | m/hr
|  |  | Vmf (10°C) | 29.4203 | m/hr
|  |  | Vmf (15°C) | 32.467 | m/hr
|  |  | Vmf (20°C) | 35.3882 | m/hr
|  |  | Vmf (25°C) | 38.1342 | m/hr
|  |  | Vmf (30°C) | 40.6669 | m/hr
|  |  | Vmf (0°C) | 9.4479 | gpm/sf
Recommended Maximum ETSW Rate ========> |  |  | Vmf (5°C) | 10.7342 | gpm/sf
*you may choose to exceed this value in favor of |  |  | Vmf (10°C) | 12.035 | gpm/sf
the Vmf for 25 degrees C during the summer |  |  | Vmf (15°C) | 13.2813 | gpm/sf
months and then revert back to this value during |  |  | Vmf (20°C) | 14.4763 | gpm/sf
the winter months. |  |  | Vmf (25°C) | 15.5996 | gpm/sf
|  |  | Vmf (30°C) | 16.6356 | gpm/sf
|  | Temp. (C) | Recommended Wash Rates (1.3*Vmf)
|  | 0 | 30.0246 | m/hr | Ratio to 20 C
|  | 5 | 34.1127 | m/hr | 0.74151
|  | 10 | 38.2464 | m/hr | 0.83136
|  | 15 | 42.2071 | m/hr | 0.91745
|  | 20 | 46.0046 | m/hr | 1
|  | 25 | 49.5745 | m/hr | 1.0776
|  | 30 | 52.867 | m/hr | 1.1492
|  | 0 | 12.2822 | gpm/sf | 0.65264
*lower backwash rates can be used |  | 5 | 13.9545 | gpm/sf | 0.74151
when water is colder to conserve |  | 10 | 15.6455 | gpm/sf | 0.83136
backwash water, with little concern |  | 15 | 17.2657 | gpm/sf | 0.91745
over decreasing cleaning efficiency |  | 20 | 18.8192 | gpm/sf | 1
Recommended Backwash Rate ===> |  | 25 | 20.2795 | gpm/sf | 1.0776
|  | 30 | 21.6263 | gpm/sf | 1.1492
*again, you can average values for sand and anthracite, or choose the higher value to be on the safe side

## 12. Air Scour Example
Air Scour Backwashing Equations for Collapse Pulsing
Source: Amirtharajah, 1991 (WaterRF Project Report)
For example:
A dual media filter with a Vmf (d90) of 15 gpm/ft^2 and an air flow rate of 2 scfm/ft^2 would require a "V" (water flow rate for combined air/water wash) of: | [5 empty] | 4.91 gpm/ft^2
1.7 (2.0)^2 + % V/(15) = 39.5
1.7*4 + % V/15 =39.5
6.8 + % V/15 = 39.5
% V/15 = 39.5 - 6.8
% V/15 = 32.7
V = 32.7 % * 15
V = .327 * 15
V = 4.91 gpm/ft^2
Sample Calculation:
For your dual media filter at 15°C, with an air flow rate of: |  |  |  | 2 | scfm/sq ft
V = | 4.245 | gpm/sf | (water flow rate)

## 13. Conversion-gpm to gpm-sf
GPM to GPM/SF to GPM Conversion Table
| Filter area : | 392 | sq. ft. |  |  | 36.4144 | sq. meters
Rise Rates
gpm | gpm/sf | L/s | gpm/sf | gpm | L/s | m/min | ft/min
12500 | 31.8878 | 788.5417 | 20 | 7840 | 494.5733 | 0.81491 | 2.6737
12000 | 30.6122 | 757 | 19.5 | 7644 | 482.209 | 0.79453 | 2.6069
11500 | 29.3367 | 725.4583 | 19 | 7448 | 469.8447 | 0.77416 | 2.54
11000 | 28.0612 | 693.9167 | 18.5 | 7252 | 457.4803 | 0.75379 | 2.4732
10500 | 26.7857 | 662.375 | 18 | 7056 | 445.116 | 0.73342 | 2.4063
10000 | 25.5102 | 630.8333 | 17.5 | 6860 | 432.7517 | 0.71304 | 2.3395
9500 | 24.2347 | 599.2917 | 17 | 6664 | 420.3873 | 0.69267 | 2.2727
9000 | 22.9592 | 567.75 | 16.5 | 6468 | 408.023 | 0.6723 | 2.2058
8500 | 21.6837 | 536.2083 | 16 | 6272 | 395.6587 | 0.65193 | 2.139
8000 | 20.4082 | 504.6667 | 15.5 | 6076 | 383.2943 | 0.63155 | 2.0721
7500 | 19.1327 | 473.125 | 15 | 5880 | 370.93 | 0.61118 | 2.0053
7000 | 17.8571 | 441.5833 | 14.5 | 5684 | 358.5657 | 0.59081 | 1.9384
6500 | 16.5816 | 410.0417 | 14 | 5488 | 346.2013 | 0.57044 | 1.8716
6000 | 15.3061 | 378.5 | 13.5 | 5292 | 333.837 | 0.55006 | 1.8048
5500 | 14.0306 | 346.9583 | 13 | 5096 | 321.4727 | 0.52969 | 1.7379
5000 | 12.7551 | 315.4167 | 12.5 | 4900 | 309.1083 | 0.50932 | 1.6711
4500 | 11.4796 | 283.875 | 12 | 4704 | 296.744 | 0.48894 | 1.6042
4000 | 10.2041 | 252.3333 | 11.5 | 4508 | 284.3797 | 0.46857 | 1.5374
3500 | 8.9286 | 220.7917 | 11 | 4312 | 272.0153 | 0.4482 | 1.4705
3000 | 7.6531 | 189.25 | 10.5 | 4116 | 259.651 | 0.42783 | 1.4037
2500 | 6.3776 | 157.7083 | 10 | 3920 | 247.2867 | 0.40745 | 1.3369
2000 | 5.102 | 126.1667 | 9.5 | 3724 | 234.9223 | 0.38708 | 1.27
1500 | 3.8265 | 94.625 | 9 | 3528 | 222.558 | 0.36671 | 1.2032
1000 | 2.551 | 63.0833 | 8.5 | 3332 | 210.1937 | 0.34634 | 1.1363
500 | 1.2755 | 31.5417 | 8 | 3136 | 197.8293 | 0.32596 | 1.0695
400 | 1.0204 | 25.2333 | 7.5 | 2940 | 185.465 | 0.30559 | 1.0026
300 | 0.76531 | 18.925 | 7 | 2744 | 173.1007 | 0.28522 | 0.9358
200 | 0.5102 | 12.6167 | 6.5 | 2548 | 160.7363 | 0.26484 | 0.86896
100 | 0.2551 | 6.3083 | 6 | 2352 | 148.372 | 0.24447 | 0.80211
80 | 0.20408 | 5.0467 | 5.5 | 2156 | 136.0077 | 0.2241 | 0.73527
60 | 0.15306 | 3.785 | 5 | 1960 | 123.6433 | 0.20373 | 0.66843
40 | 0.10204 | 2.5233 | 4.5 | 1764 | 111.279 | 0.18335 | 0.60159
20 | 0.05102 | 1.2617 | 4.245 | 1664.0322 | 104.9727 | 0.17296 | 0.56749
10 | 0.02551 | 0.63083 | 3.745 | 1468.0322 | 92.6084 | 0.15259 | 0.50065
5 | 0.012755 | 0.31542 | 3.245 | 1272.0322 | 80.244 | 0.13222 | 0.43381
3 | 0.0076531 | 0.18925 | 2.745 | 1076.0322 | 67.8797 | 0.11185 | 0.36696
1 | 0.002551 | 0.063083 | 2.245 | 880.0322 | 55.5154 | 0.091473 | 0.30012

## 14. Constants vs Temperature
Temperature (°C) | mu (dynamic viscosity) mPa*s | mu (g/cm s) | rho (density) g/cm^3
0 | 1.781 | 0.01781 | 0.9998
5 | 1.519 | 0.01519 | 1
10 | 1.307 | 0.01307 | 0.9997
15 | 1.139 | 0.01139 | 0.9991
20 | 1.002 | 0.01002 | 0.9982
25 | 0.89 | 0.0089 | 0.997
30 | 0.798 | 0.00798 | 0.9957

## 15. Typical Media Values
TYPICAL Media Values (Textbook):
Media: | Sand | Anthracite | GAC | Garnet | Illmenite
Density | 2.65 | 1.45-1.73 | 1.3-1.5 | 3.6-4.2 | 4.2-4.6
Porosity | .42-.47 | .56-.60 | 0.5 | .45-.55 | --
Source: Water Quality and Treatment, 5th Ed. (1999)
Media: | Sand | Anthracite | GAC | Garnet | Garnet**
Density | 2.55-2.65 | 1.5-1.75 |  | 4-4.3 | 4
Porosity | .4-.45 | .5-.55 |  |  | .45-.55
ES | .4-.55 | .8-1.1 |  |  | .2-.3
UC | 1.3-1.8 |  |  |  | 1.5-1.8
Depth | 6-12" | 18-30" |  |  | 4"
UC-deep bed: |  | 1.2-1.3
Depth-deep bed: |  | 4-6'
Source: Water Treatment Plant Design, 3rd Ed. (1998)
**Source: Internet websites:
http://www.northerngravel.com/products.html
http://www.usace.army.mil/publications/eng-tech-ltrs/etl1110-1-159/a-iii.pdf
others as references

## 16. pOH vs. pH
Constant pH of 7.0
Temperature (°C) | pKw | pH | pOH
0 | 14.94 | 7 | 7.94
5 | 14.73 | 7 | 7.73
10 | 14.53 | 7 | 7.53
15 | 14.35 | 7 | 7.35
20 | 14.17 | 7 | 7.17
25 | 14 | 7 | 7
30 | 13.83 | 7 | 6.83
35 | 13.68 | 7 | 6.68
40 | 13.53 | 7 | 6.53
Constant pH of 7.5
Temperature (°C) | pKw | pH | pOH
0 | 14.94 | 7.5 | 7.44
5 | 14.73 | 7.5 | 7.23
10 | 14.53 | 7.5 | 7.03
15 | 14.35 | 7.5 | 6.85
20 | 14.17 | 7.5 | 6.67
25 | 14 | 7.5 | 6.5
30 | 13.83 | 7.5 | 6.33
35 | 13.68 | 7.5 | 6.18
40 | 13.53 | 7.5 | 6.03
Constant pOH of 7.5 |  |  |  | Constant pOH of 7.0 |  |  |  | Constant pOH of 6.5 |  |  |  | Constant pOH (vs. pH 6.5 at 22° C) |  |  |  | Good idea!
Temperature (°C) | pKw | pH | pOH | Temperature (°C) | pKw | pH | pOH | Temperature (°C) | pKw | pH | pOH | Temperature (°C) | pKw | pH | pOH
0 | 14.94 | 7.44 | 7.5 | 0 | 14.94 | 7.94 | 7 | 0 | 14.94 | 8.44 | 6.5 | 0 | 14.94 | 7.34 | 7.6
5 | 14.73 | 7.23 | 7.5 | 5 | 14.73 | 7.73 | 7 | 5 | 14.73 | 8.23 | 6.5 | 5 | 14.73 | 7.13 | 7.6
10 | 14.53 | 7.03 | 7.5 | 10 | 14.53 | 7.53 | 7 | 10 | 14.53 | 8.03 | 6.5 | 10 | 14.53 | 6.93 | 7.6
15 | 14.35 | 6.85 | 7.5 | 15 | 14.35 | 7.35 | 7 | 15 | 14.35 | 7.85 | 6.5 | 15 | 14.35 | 6.75 | 7.6
20 | 14.17 | 6.67 | 7.5 | 20 | 14.17 | 7.17 | 7 | 20 | 14.17 | 7.67 | 6.5 | 20 | 14.17 | 6.57 | 7.6
25 | 14 | 6.5 | 7.5 | 25 | 14 | 7 | 7 | 25 | 14 | 7.5 | 6.5 | 22 | 14.102 | 6.502 | 7.6
30 | 13.83 | 6.33 | 7.5 | 30 | 13.83 | 6.83 | 7 | 30 | 13.83 | 7.33 | 6.5 | 25 | 14 | 6.4 | 7.6
35 | 13.68 | 6.18 | 7.5 | 35 | 13.68 | 6.68 | 7 | 35 | 13.68 | 7.18 | 6.5 | 30 | 13.83 | 6.23 | 7.6
40 | 13.53 | 6.03 | 7.5 | 40 | 13.53 | 6.53 | 7 | 40 | 13.53 | 7.03 | 6.5 | 35 | 13.68 | 6.08 | 7.6
[12 empty] | 40 | 13.53 | 5.93 | 7.6
Neutral pH
Temperature (°C) | pKw | pH | pOH | [8 empty] | Constant pH of 6.5 (relative to 22° C) |  |  |  | Bad idea!
0 | 14.94 | 7.47 | 7.47 | [8 empty] | Temperature (°C) | pKw | pH | pOH
5 | 14.73 | 7.365 | 7.365 | [8 empty] | 0 | 14.94 | 6.5 | 8.44
10 | 14.53 | 7.265 | 7.265 | [8 empty] | 5 | 14.73 | 6.5 | 8.23
15 | 14.35 | 7.175 | 7.175 | [8 empty] | 10 | 14.53 | 6.5 | 8.03
20 | 14.17 | 7.085 | 7.085 | [8 empty] | 15 | 14.35 | 6.5 | 7.85
25 | 14 | 7 | 7 | [8 empty] | 20 | 14.17 | 6.5 | 7.67
30 | 13.83 | 6.915 | 6.915 | [8 empty] | 22 | 14.102 | 6.502 | 7.6
35 | 13.68 | 6.84 | 6.84 | [8 empty] | 25 | 14 | 6.5 | 7.5
40 | 13.53 | 6.765 | 6.765 | [8 empty] | 30 | 13.83 | 6.5 | 7.33
[12 empty] | 35 | 13.68 | 6.5 | 7.18
[12 empty] | 40 | 13.53 | 6.5 | 7.03

## 17. Contact Info
The Extended Terminal Subfluidization Wash (ETSW) procedure was developed by Dr. James Amburgey
during his Ph.D. Research at Georgia Tech under the guidance of Dr. Appiah Amirtharajah a very long time ago.
Dr. Amburgey may be contacted to consult on projects involving the ETSW procedure via the information below:
James E. Amburgey, Ph.D., P.E.
UNC Charlotte
Dept. of Civil & Environmental Engrg.
9201 University City Blvd.
Charlotte, NC 28223-0001
Ph. (704) 687-1214 | Water Treatment Research, Inc.
E-mail: jeamburg@uncc.edu
* Please check any peer-reviewed journals that you have access to for the most
recent research findings regarding the ETSW procedure and related topics.